DEPARTMENT OF LICENSING AND REGULATORY AFFAIRS

- DIRECTOR’S OFFICE

- CONSTRUCTION CODE

- Filed with the secretary of state on

These rules become effective 120 days after filing with the secretary of state

(By authority conferred on the director of the department of licensing and regulatory affairs by section 4 of the Stille-Derossett-Hale single state construction code, 1972 PA 230, MCL 125.1504, and Executive Reorganization Order Nos. 2003-1, 2008-4, and 2011-4, MCL 445.2011, 445.2025, and 445.2030)

R 408.30701, R 408.30711, R 408.30715, R 408.30717, R 408.30718, R 408.30719, R 408.30741c, R 408.30757, and R 408.30791 of the Michigan Administrative Code are amended, R 408.30712, R 408.30726, R 408.30727, R 408.30729, and R 408.30755 are added, and R 408.30720 and R 408.30757a are rescinded as follows:

- PART 7.  PLUMBING CODE

AMENDMENTS AND ADDITIONS TO BASIC PLUMBING CODE

R 408.30701  Applicable code.

Rule 701.  Rules governing the installation, replacement, alteration, relocation, and use of plumbing systems or plumbing materials shall be those contained in the international plumbing code, 20152018 edition, including appendices A, B, C, D, E, F, and G, and HF, except for sections 102.10, 102.11, 103.1 to 103.3,103.4, 103.4.1, 104.2, 104.5 to 104.7, 105.1, 105.3 to 105.3.3, 106.1.1, 106.1.2, 106.3, 106.3.2, 106.3.3, 106.5.5, 106.6.1, 106.6.2, 106.6.3, 107.2.5, 107.2.5.1, 107.2.5.2, 107.2.5.3, 108.3, 108.5, 109.1, 109.2 to 109.7, 312.1.1, 404.2, 404.3, 602.3 to 602.3.5.1, 608.17 to 608.17.8608.18 to 608.18.8, 712.3.3.1, 712.3.3.2, 715.1 to 715.4, 802.4.3.1,716.1 to 716.4, 1106.3, 1106.6, 1301 to 1304.4.2, 1401 to 1403.2.1 and tables 608.18.1, 1106.3, and 1106.6.  With the exceptions noted, the code is adopted in these rules by reference.  All references to the International Building Code, International Residential Code, International Energy Conservation Code, International Electrical Code, International Mechanical Code, and International Plumbing Code mean the Michigan Building Code, Michigan Residential Code, Michigan Uniform Energy Code, Michigan Electrical Code, Michigan Mechanical Code, and Michigan Plumbing Code respectively.  The code is available for inspection at the Lansing office of the Michigan department of licensing and regulatory affairs, bureau of construction codes.  The code may be purchased from the International Code Council, through the bureau’s website at www.michigan.gov/bcc for$76.00$83.00 for each code book.

R 408.30711  Title and scope.

Rule 711.  Sections 101.1, and 101.2, and 101.3 of the code are amended to read as follows:

101.1.  Title.  This part shall be known as the Michigan plumbing code and is hereinafter referred to as “the plumbing code” or “the code.”  This part shall control all matters concerning the installation, replacement, alteration, relocation, and use of plumbing systems or plumbing materials as herein defined and shall apply to existing or proposed buildings and structures in the state.

101.2.  Scope.  The design and installation of plumbing systems, including sanitary and storm drainage, sanitary facilities, medical gas systems, water supplies, water service, and storm water and sewage disposal in and exiting buildings, shall comply with the requirements of the code.  The design and installation of gas piping, chilled water piping in connection with refrigeration process and comfort cooling, and hot water piping in connection with building heating systems shall conform to the Michigan mechanical code.  The design and installation of all fire sprinkler systems and standpipe systems shall conform to the Michigan building code.  Water and drainage connections to such installations shall be made in accordance with the requirements of the code.

Exception:  Detached 1-and 2-family dwellings and multiple single-family dwellings (townhouses) not more than 3 stories high with separate means of egress and their accessory structures shall comply with the Michigan residential code.

101.3.  Intent.  The purpose of this code is to establish minimum standards to provide a reasonable level of safety, health, property protection and public welfare by regulating and controlling the design, construction, installation, quality of materials, location, and operation and maintenance or use of plumbing equipment and systems.  The act takes precedence over all provisions of this code.

R 408.30712  Temporary equipment, systems and uses.

Rule 712.  Section 110.1 of the code is amended to read as follows:

110.1.  General.  An authority having jurisdiction may issue a permit for temporary equipment, systems, and uses.  Such permits shall be limited as to time of service but shall not be permitted for more than 180 days.  The authority having jurisdiction may grant a 180-day extension of the original permit time period of 180 days, upon presentation by the permittee of a satisfactory reason for failure to start or complete the work or activity authorized by the permit.

R 408.30715  Permits.

Rule 715.  Sections 106.4, 106.5.3, and 106.5.4 of the code are amended to read as follows:

106.4.  By whom application is made.

(1)  Application for a permit shall be made by a plumbing contractor licensed in accordance with 2002 PA 733, MCL 338.3511 to 338.3569.

Exceptions:

1.  Water service permits.

2.  Building sewer and private sewer permits.

3.  Minor repair.

(2)  A plumbing contractor shall do both of the following:

(a) Be active in the business of serving the public as a plumbing contractor in a county, city, village, or township in this state.

(b) Operate 1 or more branches in this state bearing the same firm name, where a licensed master plumber is in charge and has the responsibility of supervision at each branch.  The names of the authorized master plumbers representing a firm shall be on record with the state plumbing board.

(3) To become a plumbing contractor, an applicant shall file an application on a form furnished by the state plumbing board and file with the board at Lansing, Michigan.  An incomplete application will be returned to the applicant.

106.5.3.  Expiration.  Each permit issued by the code official under the provisions of the code shall expire by limitation and become null and void if the work authorized by this permit is not commenced within 180 days from the date of such permit, or if the work authorized by this permit is suspended or abandoned at any time after the work is commenced for a period of 180 days.  Before this work may be recommenced, the permit shall be reinstated if the code has not changed.  If the code has changed and the work was not started, a new permit shall be first obtained for such work, provided no changes have been made or will be made in the original construction document for this work and provided further that the suspension or abandonment has not exceeded 1 year.

106.5.4.  Extensions.  Any permittee holding an unexpired permit shall have the right to apply for an extension of the time within which the permittee will commence work under that permit when work is unable to be commenced within the time required by this section for good and satisfactory reasons.  The code official shall extend the time for action by the permittee for a period not exceeding 180 days if there is reasonable cause.  No permit shall be extended more than once. Application and extensions.  The authority having jurisdiction may grant a 180-day extension of the original permit time period of 180 days, upon presentation by the permittee of a satisfactory reason for failure to start or complete the work or activity authorized by the permit.

R 408.30717  Duties and powers of code officialRight of entry.

Rule 717.  Section 104.1104.4 of the code is amended to read as follows:

104.1  General104.4  Right of entry.  The code official shall enforce all of the provisions of the code and shall act on any question relative to the installation, alteration, repair, maintenance, or operation of all plumbing systems, devices, and equipment except as specifically provided for by statutory requirements or as provided for in sections 104.3 to 104.7. If a building or premises is occupied, the code official shall present his or her credentials to the occupant and request entry. If a building or premises is unoccupied, the code official shall first make a reasonable effort to locate either the owner, the owner’s authorized agent or other person having care or control of the building or premises and request entry. If entry is refused, the code official has recourse to every remedy provided by law to secure entry.

When a code official has first obtained a proper inspection warrant or other remedy provided by law to secure entry, the owner, owner’s authorized agent or occupant or person having charge, care or control of the building or premises shall not fail or neglect, after a proper request is made as provided in this rule, to permit the code official prompt entry into the building or premises to inspect or examine the building or premises pursuant to this code.

R 408.30718  Violation penalties.

Rule 718.  Section 108.4 of the code is amended to read as follows:

108.4.  Violation penalties.  A person who violates a provision of the code, who fails to conform with any of the requirements thereof, or who erects, installs, alters, or repairs plumbing work in violation of the approved construction documents or directive of the enforcing agency, or a permit or certificate issued under the provisions of the code shall be assessed a fine in accordance with the act and 2002 PA 733, MCL 338.3511 to 338.3569shall be subject to review and may result in licensing action pursuant to the skilled trades regulation act, 2016 PA 407, MCL 339.5101 to 339.6133.

R 408.30719  Stop work ordersInspections and testing.

Rule 719.  Section 108.5Sections 107.1 and 107.2.1 of the code is are amended to read as follows:

108.5.  Stop work orders.107.1.  General.  Notice shall be in accordance with the act.  A person who is served with a stop work order, except for work that the person is directed to perform to remove a violation or unsafe condition is subject to the penalty provisions prescribed by the act.The code official is authorized to conduct the inspections needed to determine compliance with the provisions of this code.  Construction or work that requires a permit is subject to inspections by the code official. This construction or work must remain accessible and exposed for inspection until approved.  The permit applicant shall ensure that the work remain accessible and exposed for inspection.  Neither the code official nor the jurisdiction shall be liable for any expense related to the removal or replacement of any material necessary to allow an inspection.

107.2.1.  Inspection requests.  It shall be the duty of the holder of the permit or their duly authorized agent to notify the code official when work is ready for inspection.

R 408.30720  Means of appeal Rescinded.

Rule 720.  Section 109.1 of the code is amended to read as follows:

109.1  Means of appeal An interested person may appeal a decision of the enforcing agency to the board of appeals in accordance with the act.  An application for appeal shall be based on a claim that the true intent of the code or the rules governing construction have been incorrectly interpreted, the provisions of the code do not apply, or an equal or better form of construction is proposed.  The decision of a local board of appeals may be appealed to the construction code commission in accordance with the act and time frames

R 408.30726  Building sewer.

Rule 726.  Table 702.3 and section 703.1 of the code are amended to read as follows:

Table 702.3

BUILDING SEWER PIPE

| MATERIAL | STANDARD |
| --- | --- |
| Acrylonitrile butadiene styrene (ABS) plastic pipe in IPS diameters, including Schedule 40, DR 22 (PS 200) and DR 24 (PS 140); with a solid, cellular core or composite wall | ASTM D2661; ASTM F628; ASTM F1488; CSA B181.1 |
| Acrylonitrile butadiene styrene (ABS) plastic pipe in sewer and drain diameters, including SDR 42 (PS 20), PS 35, SDR 35 (PS 45), PS 50, PS 100, PS 140, SDR 23.5 (PS 150) and PS 200; with a solid, cellular core or composite wall. | ASTM F1488; ASTM D2751 |
| Cast-iron pipe | ASTM A74; ASTM A888; CISPI 301 |
| Concrete pipe | ASTM C14; ASTM C76; CSA A257.1M; CSA A257.2M |
| Copper or copper-alloy tubing (Type K or L) | ASTM B75; ASTM B88; ASTM B251 |
| Polyethylene (PE) plastic pipe (SDR-PR) | ASTM F714 |
| Polypropylene (PP) plastic pipe | ASTM F2736; ASTM F2764; CSA B182.13 |
| Polyvinyl chloride (PVC) plastic pipe in IPS diameters, including Schedule 40, DR 22 (PS 200) and DR 24 (PS 140); with a solid, cellular core or composite wall | ASTM D2665; ASTM F891; ASTM F1488 |
| Polyvinyl chloride (PVC) plastic pipe in sewer and drain diameters, including PS 25, SDR 41 (PS 28), PS 35, SDR 35 (PS 46), PS 50, PS 100, SDR 26 (PS 115), PS 140 and PS 200; with a solid, cellular core or composite wall. | ASTM F891; ASTM F1488; ASTM D3034; CSA B182.2; CSA B182.4 |
| Polyvinyl chloride (PVC) plastic pipe with a 3.25-inch O.D. and a solid, cellular core or composite wall | ASTM D2949; ASTM F1488 |
| Polyvinylidene fluoride (PVDF) plastic pipe | ASTM F1673; CSA B181.3 |
| Stainless steel drainage systems, Types 304 and 316L | ASME A112.3.1 |
| Vitrified clay pipe | ASTM C4; ASTM C700 |

For SI: 1 inch = 25.4 mm.

703.2  Drainage pipe in filled ground.  Where a building sewer or building drain is installed on filled or unstable ground, the drainage pipe shall conform to one of the standards for ABS plastic pipe, cast-iron pipe, copper or copper-alloy tubing, or PVC plastic pipe indicated in Table 702.3.

R 408.30727 Water distribution pipe.

Rule 727. Table 605.4 of the code is amended to read as follows:

Table 605.4

WATER DISTRIBUTION PIPE

| MATERIAL | STANDARD |
| --- | --- |
| Chlorinated polyvinyl chloride (CPVC) plastic pipe and tubing | ASTM D2846; ASTM F441; ASTM F442; CSA B137.6 |
| Chlorinated polyvinyl chloride/aluminum/chlorinated polyvinyl chloride (CPVC/AL/CPVC) | ASTM F2855 |
| Copper or copper-alloy pipe | ASTM B42; ASTMB302; ASTM B43 |
| Copper or copper-alloy tubing (Type K, WK, L, WL, M or WM) | ASTM B75; ASTM B88; ASTM B251; ASTM B447 |
| Cross-linked polyethylene (PEX) plastic tubing | ASTM F876; CSA B137.5 |
| Cross-linked polyethylene/aluminum/cross-linked polyethylene (PEX-AL-PEX) pipe | ASTM F1281; ASTM F2262; CSA B137.10 |
| Cross-linked polyethylene/aluminum/high-density polyethylene (PEX-AL-HDPE) | ASTM F1986 |
| Ductile iron pipe | AWWA C151/A21.51; AWWA C115/A21.15 |
| Polyethylene/aluminum/polyethylene (PE-AL-PE) composite pipe | ASTM F1282 |
| Polyethylene of raised temperature (PE-RT) plastic tubing | ASTM F2769; CSA B137.158 |
| Polypropylene (PP) plastic pipe or tubing | ASTM F2389; CSA B137.11 |
| Stainless steel pipe (Type 304/304L) | ASTM A312; ASTM A778 |
| Stainless steel pipe (Type 316/316L) | ASTEM A312; ASTEM A778 |

R 408.30729  Water service pipe.

Rule 729.  Table 605.3 and section 609.3 of the code are amended to read as follows:

Table 605.3

Water Service Pipe

| MATERIAL | STANDARD |
| --- | --- |
| Acrylonitrile butadiene styrene (ABS) plastic pipe | ASTM D1527; ASTM D2282 |
| Chlorinated polyvinyl chloride (CPVC) plastic pipe | ASTM D2846; ASTM F441; ASTM F442; CSA B137.6 |
| Chlorinated polyvinyl chloride/aluminum/chlorinated polyvinyl chloride (CPVC/AL/CPVC) | ASTM F2855 |
| Copper or copper-alloy pipe | ASTM B42; ASTM B302 |
| Copper or copper-alloy tubing (Type K, WK, L, WL, M or WM) | ASTM B75; ASTM B88; ASTM B251; ASTM B447 |
| Cross-linked polyethylene (PEX) plastic pipe and tubing | ASTM F876; AWWA C904; CSA B137.5 |
| Cross-linked polyethylene/aluminum/cross-linked polyethylene (PEX-AS-PEX) pipe | ASTM F1281; ASTM F2262; B137.10 |
| Cross-linked polyethylene/aluminum/high-density polyethylene (PEX-AL-HDPE) | ASTM F1986 |
| Ductile iron water pipe | AWWA C151/A21.51; AWWA C115/A21.15 |
| Polyethylene (PE) plastic pipe | ASTM D2239; ASTM D3035; AWWA C901; CSA B137.11 |
| Polyethylene (PE) plastic tubing | ASTM D2737; AWWA C901; CSA B137.1 |
| Polyethylene/aluminum/polyethylene (PE-AL-PE) pipe | ASTM F1282; CSA B 137.9 |
| Polyethylene of raised temperature (PE-RT) plastic tubing | ASTM F2769; CSA B137.18 |
| Polypropylene (PP) plastic pipe or tubing | ASTM F2389; CSA B137.11 |
| Polyvinyl chloride (PVC) plastic pipe | ASTM D1785; ASTM D2241; ASTM D2672; CSA B137.3 |
| Stainless steel pipe (Type 304/304L) | ASTM A312; ASTM A778 |
| Stainless steel pipe (Type 316/316L) | ASTM A312; ASTM A778 |
| Chlorinated polyvinyl chloride (CPVC) plastic pipe and tubing | ASTM D2846; ASTM F441; ASTM F442; CSA B137.6 |
| Chlorinated polyvinyl chloride/aluminum/chlorinated polyvinyl chloride (CPVC/AL/CPVC) | ASTM F2855 |
| Copper or copper-alloy pipe | ASTM B-42; ASTM B302; ASTM B43 |
| Copper or copper-alloy tubing (Type K, WK, L, WL, M or WM) | ASTM B75; ASTM B88; ASTM B251; ASTM B447 |
| Cross-linked polyethylene (PEX) plastic tubing | ASTM F876; CSA B137.5 |
| Cross-linked polyethylene/aluminum/cross-linked polyethylene (PEX-AL-PEX) pipe | ASTM F1281; ASTM F2262; CSA B137.10 |
| Cross-linked polyethylene/aluminum/high-density polyethylene (PEX-AL-HDPE) | ASTM F1986 |
| Ductile iron pipe | AWWA C151/A21.51; AWWA C115/A21.15 |
| Polyethylene/aluminum/polyethylene (PE-AL-PE) composite pipe | ASTM F1282 |
| Polyethylene of raised temperature (PE-RT) plastic tubing | ASTM F2769; CSA B137.158 |
| Polypropylene (PP) plastic pipe or tubing | ASTM F2389; CSA B137.11 |
| Stainless steel pipe (Type 304/304L) | ASTM A312; ASTM A778 |
| Stainless steel pipe (Type 316/316L) | ASTM A312; ASTM A778 |

609.3 Hot water.  Hot water shall be provided to supply all of the hospital fixture, kitchen, and laundry requirements.  Special fixtures and equipment shall have hot water supplied at a temperature specified by the manufacturer.  The hot water system shall be installed in accordance with section 607.

R 408.30741c  Connections to automatic fire sprinkler systems and standpipe systems.

Rule 741c.  Section 608.1617.4 of the code is amended to read as follows:

608.1617.4.  Connections to automatic fire sprinkler systems and standpipe systems.  The potable water supply to automatic fire sprinkler and standpipe systems shall be protected against backflow by a double check backflow prevention assembly, a double check fire protection backflow prevention assembly, or a reduced pressure principle fire protection backflow prevention assembly.

Exception:  Isolation of the water distribution system is not required for deluge, preaction, or dry pipe systems.

R 408.30755  Storm drainage.

Rule 755.  Table 1102.4 of the code is amended to read as follows:

TABLE 1102.4

BUILDING STORM SEWER PIPE

| MATERIAL | STANDARD |
| --- | --- |
| Acrylonitrile butadiene styrene (ABS) plastic pipe in IPS diameters, including Schedule 40, DR 22 (PS 200) and DR 24 (PS 140); with a solid, cellular core or composite wall. | ASTM D2661; ASTM F628; ASTM F1488; CSA B181.1; CSA B182.1 |
| Cast-iron pipe | ASTM A74; ASTM A888; CISPI 301 |
| Concrete pipe | ASTM C14; ASTM C76; CSA A257.1M; CSA A257.2M |
| Copper or copper-alloy tubing (Type K, L, M or DWV) | ASTM B75; ASTM B88; ASTM B251; ASTM B306 |
| Polyethylene (PE) plastic pipe | ASTM F667; ASTM F2306/F2306; ASTM F2648/F2548M |
| Polypropylene (PP) plastic pipe | ASTM F2736; ASTM F2764; CSA B182.13 |
| Vitrified clay pipe | ASTM C4; ASTM C700 |
| Stainless steel drainage systems, Type 316L | ASME A112.3.1 |

R 408.30757  Horizontal drains within building and building sewers.

Rule 757.  SectionSections  708.3 and 708.3.4 of the code are being added to read as follows:

708.3  Where required.  Cleanouts shall be located in accordance with sections 708.3.1, 708.3.3 to 708.3.5.

708.3.1. Horizontal drains within building and building sewers. All horizontal drains within buildings and building sewers shall be provided with cleanouts located not more than 100 feet (30 480mm) apart.

For underground piping that is more than 10 inches in diameter, manholes shall be provided and located at every major change of direction, grade, elevation, or size of pipe or at intervals of not more than 400 feet (12 1920 mm). Metal covers shall be provided for the manholes and shall be of sufficient weight to meet local traffic and loading conditions.

Within buildings, manhole covers shall be gastight and the manhole shall be vented with not less than a 4- inch (102 mm) pipe.

708.3.4.  Base of stack.  A cleanout shall be provided at the base of each waste or soil stack.

- R 408.30757a Discharge pipe and fittingsRescinded.

- Rule 757a.  Section 712.3.3 of the code is added to read as follows:

712.3.3.  Discharge pipe and fittings.  Discharge piping and fittings shall be constructed of approved materials.

- R 408.30791  Definitions.

Rule 791.  (1)  Section 202 of the code is amended to amend the definition of code official and add the definitions of the act and plumbing contractor.

(2)  “Act” means 1972 PA 230, MCL 125.1501 to 125.1531, and is known as the Stille-DeRossett-Hale single state construction code act.

(3)  “Code official” means the person appointed and employed by a governmental subdivision charged with the administration and enforcement of the state code or codes and registered in accordance with the requirements of 1986 PA 54, MCL 338.2301 to 338.2313an individual, who is registered pursuant to article 10 of the skilled trades act, 2016 PA 407, MCL 339.6001 to 339.6023, and who is authorized to conduct the inspections needed to determine compliance with the provisions of this code. Construction or work that requires a permit shall be subject to inspection by the code official. This construction or work shall remain visible and be accessible for inspection purposes until approved.

(4)  "Plumbing contractor" means a person who is licensed in accordance with 2002 PA 733, MCL 338.3511 to 338.356